## Sheet1
Instructions | If you got this off of jackdanmayer.com you might want to email me and ask if I have an updated version. The newest is not always on the web - although I try.
There are four sections below. The Variables and Constants is where you enter your basic system info. The Power Created section calculates your solar and generator power on a daily basis.
The tables in Power Created allow you to work in AmpHours or WattHours. I recommend WattHours. In the end it is simpler. If you are using high voltage panels you MUST work in watthours
The Power Used section estimates your power consumption for a 24hr period. It takes into account parasitic draw and the residential refrigerator you specified, and estimates the rest of the "house" loads.
The Power Stored section is used for your battery bank.
Enter the items specific to your situation in the variables and constants area. The orange shaded items are changeable. The rest are not. The parasitic draw is an average that works for
most people, but if you have a more accurate number, please update it. The solar panel rating should be changed for your panels. As should the refrigerator electrical consumption.
This will give you an "idea" of how your system will operate, but you will have to play with the numbers.
There are three key figures here. "Total Power Used", the "Power Created" table, and the battery bank "Storage" table. Vary the number of panels and battery bank size to make sure it covers your
projected "Total Power Used" number.
Variables and Constants | [8 empty] | Formulas
volts=watts/amps
Variable that can be changed and will effect calculations | [9 empty] | amps=watts/volts
watts=amps*Volts
RV parasitic draw/hr | 63 | 5 | Orange is in DC amps, calculated is in watt-hours | [6 empty] | 1kW=83.33 Ahs
Solar panel rating (Watts) | 205 |  | If working in WattHours you only need the panel watts. Don't use Imp.
Solar panel rating (Imp) | 5.7 |  | If working in AmpHours with nominal 12-volt panels enter Imp as well as panel watts. Don't use this for high voltage panels.
Charger output | 125 |  | Change for your charger size. You only get peak output during bulk with low batteries.
Hours solar | 5 |  | No higher…might make less.
Solar Efficiency factor | 0.85 |  | Accounts for wire loss, battery conversion inefficiencies, flat panels, etc.
Solar Boost factor | 0.1 |  | Assumes MPPT controller. It is 0 with a PWM controller
Gal. Avail in 40# tank | 9.3
Gen. Propane gal/hr | 0.6 |  | Generator propane use. Modify for your genset. Use something around the 50% load rating. You can change this to diesel use, but be careful calculations work.
Power Created
Use the table below as an "estimate" of the number of panels and genset time required to build the battery bank up to a zero deficit each day. The "Total Power Used" number must be restored before the
battery bank deficit hits 50%. The "Days on Tank" number is for propane gensets. It will not apply if you substitute diesel or gas instead of propane.
Total Ah gain from solar and generator at various combinations
|  |  |  | Generator Gain (Propane Genset) | [5 empty] | Generator power gains are very dependent on battery type and deficit. Once Bulk charging tapers
|  |  | Run Hours | 0.5 | 1 | 1.5 | 2 | 2.5 | 3 | down there is no benefit to running the genset for just charging. Solar charging is more efficient
|  |  | AmpHours | 50 | 81.25 | 100 | 112.5 | 118.75 | 125 | during Absorption and Float. The gain from genset is reduced on longer runs due to coming out of Bulk mode
|  |  | WattHours | 720 | 1170 | 1360 | 1496.25 | 1579.375 | 1662.5 | WattHours will be conservative since 13 volts was used in calculation
|  |  | Gal. used | 0.3 | 0.6 | 0.9 | 1.2 | 1.5 | 1.8
|  |  | Days on Tank | 31 | 15.5 | 10.3333 | 7.75 | 6.2 | 5.1667
| Solar AmpHours Generated Daily |  |  | 0.3: AmpHours with Generator | Tables show total power gained from solar plus various generator run times.
# Panels | Panels (Imp) | Solar Gain | Boosted
1 | 5.7 | 24.225 | 26.6475 | 76.6475 | 107.8975 | 126.6475 | 139.1475 | 145.3975 | 151.6475 | You can use this table if you use nominal 12 volt panels.
2 | 11.4 | 48.45 | 53.295 | 103.295 | 134.545 | 153.295 | 165.795 | 172.045 | 178.295 | This table does not account for high voltage panels because it uses Imp in calculations.
3 | 17.1 | 72.675 | 79.9425 | 129.9425 | 161.1925 | 172.675 | 185.175 | 191.425 | 197.675 | We recommend that you run your genset for at least a half an hour in the morning to make coffee, and
4 | 22.8 | 96.9 | 106.59 | 156.59 | 178.15 | 196.9 | 209.4 | 215.65 | 221.9 | get a "jump" on bulk charging. Especially if you have AGM batteries, which will take full charger
5 | 28.5 | 121.125 | 133.2375 | 183.2375 | 214.4875 | 233.2375 | 245.7375 | 251.9875 | 258.2375 | output if low.
6 | 34.2 | 145.35 | 159.885 | 209.885 | 241.135 | 259.885 | 272.385 | 278.635 | 284.885
7 | 39.9 | 169.575 | 186.5325 | 236.5325 | 267.7825 | 286.5325 | 299.0325 | 305.2825 | 311.5325
8 | 45.6 | 193.8 | 213.18 | 263.18 | 294.43 | 313.18 | 325.68 | 331.93 | 338.18
9 | 51.3 | 218.025 | 239.8275 | 289.8275 | 321.0775 | 339.8275 | 352.3275 | 358.5775 | 364.8275
10 | 57 | 242.25 | 266.475 | 316.475 | 347.725 | 366.475 | 378.975 | 385.225 | 391.475
| Solar WattHours Generated Daily |  |  | 0.3: WattHours with Generator | If you are using "high voltage" panels you MUST use this table and work in WattHours
# Panels | Panels (Watts) | Solar Gain | Boosted | [7 empty] | It is better to work in WattHours, anyway.
1 | 205 | 871.25 | 958.375 | 1678.375 | 2128.375 | 2318.375 | 2454.625 | 2537.75 | 2620.875
2 | 410 | 1742.5 | 1916.75 | 2636.75 | 3086.75 | 3276.75 | 3413 | 3496.125 | 3579.25
3 | 615 | 2613.75 | 2875.125 | 3595.125 | 4045.125 | 4235.125 | 4371.375 | 4454.5 | 4537.625
4 | 820 | 3485 | 3833.5 | 4553.5 | 5003.5 | 5193.5 | 5329.75 | 5412.875 | 5496
5 | 1025 | 4356.25 | 4791.875 | 5511.875 | 5961.875 | 6151.875 | 6288.125 | 6371.25 | 6454.375
6 | 1230 | 5227.5 | 5750.25 | 6470.25 | 6920.25 | 7110.25 | 7246.5 | 7329.625 | 7412.75
7 | 1435 | 6098.75 | 6708.625 | 7428.625 | 7878.625 | 8068.625 | 8204.875 | 8288 | 8371.125
8 | 1640 | 6970 | 7667 | 8387 | 8837 | 9027 | 9163.25 | 9246.375 | 9329.5
9 | 1845 | 7841.25 | 8625.375 | 9345.375 | 9795.375 | 9985.375 | 10121.625 | 10204.75 | 10287.875
10 | 2050 | 8712.5 | 9583.75 | 10303.75 | 10753.75 | 10943.75 | 11080 | 11163.125 | 11246.25
Power Used
Variable that can be changed and will effect calculations
| Watt-Hours | Ah DC | bar: 0.3
Refrigerator Draw (24hrs) | 1506 | 119.5238 |  | 0.3: Insert the Watt-Hours from the Refrigerator table below - or enter your own numbers.
Non-refrigerator draw/12 hyrs (overnight) | 1512 | 120 |  | 0.3: Enter for your RV assumes 12 hr evening period. Includes parasitic draw, TV, etc. This is a good overnight average for most people.
RV draw/12 hrs (day, parasitic) | 756 | 60 |  | 0.3: Parasitc draw for balance of 24 hr period
RV draw/12 hrs (day, non-parasitic) | 1260 | 100 |  | 0.3: This is your daytime use, not counting parasitic draw.
Total Power Used | 5034 | 399.5238
Refrigerator
Daily Usage (Watt-Hours)
| Model | Jennair # jfc2290 vtb |  | 0.9: Note: you can reduce the refrigerator usage by at least 250 watts/day by turning off the icemaker
| KWh/year | 459 |  | 0.9: An RV refrigerator uses 25-35 Ah DC on propane because of the 12V controls. This equates to about 375 watt-hours
| KWh/day | 1.2575 |  | 0.3: 1257.5342; 0.9: Turning off defrost on the residential refrigerator while boondocking will decrease power usage significantly.
| Amps@120V | 10.4795 |  | 0.9: The KWh/year figures are from the Energy Star ratings, and do not reflect adjustments to use like no defrost, no icemaker, and minimal opening.
| Amps @ 12V | 105
| Model | Samsung RB195ACPN |  | 0.9: 19 cf counter depth - all these Samsung Refrigerators can run on MSW inverters.
| KWh/year | 445
| KWh/day | 1.2192 |  | 0.3: 1219.1781
| Amps@120V | 10.1667
| Amps @ 12V | 101.6667
| Model | Samsung RF197ACPN or ACRS |  | 0.9: 32 1/4 wide. This refrigerator in actual use measured with a Kill-o-watt uses about 95 Ahs per day, or 1200 Whs, in normal use -no conservation.
| KWh/year | 445 |  | 0.9: This is consistent with it's Energy Star rating.
| KWh/day | 1.2192 |  | 0.3: 1219.1781
| Amps@120V | 10.1598
| Amps @ 12V | 101.5982
| Model | Samsung RFG238AARS |  | 0.9: 23cf counter depth 35 3/4 wide
| KWh/year | 537
| KWh/day | 1.4712 |  | 0.3: 1471.2329
| Amps@120V | 12.2603
| Amps @ 12V | 122.6027
| Model | Frigidaire FGTC2349KS 23 cf side by side with panel kit http://www.ajmadison.com/cgi-bin/ajmadison/FGTC2349KS.html
| KWh/year | 549.69
| KWh/day | 1.506 |  | 0.3: 1506
| Amps@120V | 12.55
| Amps @ 12V | 125.5
Power Stored
Battery Bank
This section will tell you how many batteries you need. Your goal should be to start each night with a full charge in your batteries, and have some reserve in case you have no solar gain that day and can not "fill".
| # Batteries | Total Amps | Total Watts | 0.3: Max Usable Amps (50%); 0.6: Useable Watts (50%); 0.9: Useable Watts (30%)
Lifeline (12 volt) | GPL-8DL | 255 | 3213 | 1.5: You can change the "Total Amps" number to reflect the battery type you are using. If using 6 volt batteries make that
| 3 | 765 | 9639 | 382.5 | 4819.5 | 2891.7 |  | the amps derived from a pair of batteries (the 3 batteries number will not be correct for 6 volt pairs). All the rest of the numbers will be calculated from that.
| 4 | 1020 | 12852 | 510 | 6426 | 3855.6 |  | It is easiest to deal with watts, here. Your total "Power Used" calculated above should ideally be less than
| 6 | 1530 | 19278 | 765 | 9639 | 5783.4 |  | the 30% number, but it is acceptable if it is between the 30%-50% range.
| 8 | 2040 | 25704 | 0.3: 1020; 0.6: 12852; 0.9: 7711.2
Note on B27: Assumes 9.3 gal avail in 40 lg tank, and 8hr runtime on tank
Note on C75: Jack_Mayer: Includes whole RV parasitic draw